Springfield Technical Community College

ACADEMIC AFFAIRS

| Course Number: | ENGY 230 | Department: | Energy Systems Technology |  |  |
| --- | --- | --- | --- | --- | --- |
| Course Title: | Energy Systems Lab 2 | Semester: | Spring | Year: | 1997 |

Objectives/Competencies

| Course Objective | Competencies |
| --- | --- |
| - Application of hot water zoning. - Operation of zone-type hot water makers. - Operation of steam boiler. - Operation of forced warm air heating system. - Operation of forced hot water heating system. - Tune-up procedure for oil burner. - Clean heat exchanger surfaces of boiler/furnace. - Trouble-shooting procedures. - Commercial burner control systems. - Honeywell 4795/7795 commercial control system. - Fireye M-Series 2 control system. - Honeywell 4140 control. - Honeywell BC 7000/Fireye E 100 controls. - Alarm circuit. - Service procedure on fire tube boiler. - Start-up procedure on boiler. - Boiler water level circuit. | - Explain how to replace electric zone valve head. - Adjust heat anticipator of thermostat. - Explain procedure for sweating valve into system. - Explain operation of aquastats used. - Wire hot water maker to aquastat control. - Describe piping to hot water maker. - Adjust temperature controls on aquastat and HWM. - Properly wire live boiler. - Explain electrical connections in wiring. - Set water level in boiler. - Check operation of low water cut-off. - Check operation of limit control. - Adjust thermostat. - Properly wire live furnace. - Adjust fan on/off settings. - Adjust high limit setting. - Perform temperature tests. - Properly wire live hot water boiler. - Adjust aquastat settings and bleed air from system. - Replace nozzle. - Adjust air handling parts. - Install burner into combustion chamber. - Perform combustion tests and adjust as needed. - Remove access panels to heat exchanger. - Analyze condition of unit. - Explain combustion chamber type/condition. - Prepare vacuum bag/filters. - Select proper brushes. - Vacuum unit. - Explain symptoms of problem. - Follow proper steps in solving problem. - Identify repairs as needed. - Repair and test system. - Properly wire Honeywell 890F control. - Perform scanner signal test. - Check safety timing. - Check flame failure response timing. - Check operation of low voltage control circuit. - Properly wire control system. - Test scanner signal. - Test air flow circuit. - Check operation of pre-purge timer. - Identify amplifier used. - Identify dip switch settings. - Explain recycle feature. - Test flame signal strength. - Explain purpose of run/test switch. - Explain purpose of BSMI circuit. - Explain operation of motor starter. - Explain purpose of low/high fire switches. - Properly wire modulation circuit. - Explain basics of microprocessor control. - Identify codes displayed by control. - Explain purpose of expansion module. - Explain flame signal readings. - Test infrared control. - Explain lockout circuit. - Explain and test flame failure response time. - Properly wire alarm circuit. - Explain operation and purpose of alarm silencer. - Remove burner from boiler. - Open front and rear doors. - Explain operation of 4-pass system. - Explain how to clean boiler. - Adjust spark ignition system - Reassemble boiler. - Explain valves to open/close. - Explain fuel selection circuit. - Start oil pump/gas system. - Explain oil/gas pressure settings. - Explain burner cycle from pre- through post purge. - Explain operation of low water cut-off. - Explain operation of automatic water feeder. - Explain service procedure on feeder valve. |